## Slide 1: AD1 - Masterplan and Buildings
QPLANT + QINFRA

## Slide 2
AD01 SCK CEN Auxiliary Buildings
Document Reference and Navigation

## Slide 3: 1. Masterplan

## Slide 4
Master Plan – MINERVA (buildings)
SCK CEN/83474410

## Slide 5
Master Plan – MINERVA (buildings)
AUB
CCB + Outside
SCK CEN/83474410

## Slide 6
MYRRHA
Reactor
Phase 1
Master Plan – MINERVA (buildings)
SCK CEN/83474410

## Slide 7
MYRRHA
Reactor
Phase 1
Master Plan – MINERVA (buildings)
SCK CEN/83474410
Coldbox Room
CCB + Outside
Level 0

## Slide 8
Master Plan – MINERVA
SCK CEN/84582975

## Slide 9
Master Plan – MINERVA (buildings)
SCK CEN/81790617
12 m available
QRB Move-in
QRB
Transport Positioning
Flatbed + Crane
QRB

## Slide 10
Master Plan – MINERVA (buildings)
Equipment – Move from South Side
SCK CEN/81504499

## Slide 11
Master Plan – MINERVA (buildings)
QRB
D = 3.5-4m
L = 11m
SCK CEN/81790617

## Slide 12
Master Plan – MINERVA (buildings)
Unload from Flatbed
Rotate
Move Sideways
Move through Roof
NEED CRANE
SCK CEN/81504499

## Slide 13: Masterplan Requirements (ACC NF)
Space between SAB and MINERVA (south) perimeter fencing for unloading and move-in (QRB specific)
Access for/to crane for lifting of QRB
  Present preference via Roof Access
  Weight <= 100 ton (expected ~70 ton)
Access for/to crane for lifting of WGS
  3 x 120 m³ gas storage vessels
Handling of instantaneous load on ground (QRB specific) – Road/Flat surfaces

## Slide 14: Building Architecture

## Slide 15: Nuclear Facilities (ACC NF)
Fixed Building dimensions!
AUB + CCB
CCB + Gas storage
Coldbox

## Slide 16: Separate Cryogenic Compressor Building
Building design ready for start of detailed-design-for-procurement
CCB+Gas Storage
SCK CEN/81503739

## Slide 17: Nuclear Facilities (ACC NF)
CCB Cros-section
SCK CEN/81505150
Note Sloping Roof

## Slide 18: CCB
CCB Cros-section
SCK CEN/81506075
WCS
Dedicated Electrical Room for WCS

## Slide 19: CCB
WCS – Room detail
Door Access for biggest equipment – HP compressor Skids
Noise Abatement (75 dB loudest equipment)
Design to prevent oil (oil lubricated compressors) contamination to outside
  Individual drip pans for HP and PVPS TBD

## Slide 20: Nuclear Facilities (ACC NF)
Gas Storage (outside)
Space for 3x120 m³ Helium storage vessels (WGS)
Space for 1x30 ton Liquid Nitrogen and Evaporator (Not ACC NF scope
Access for truck inside and/or via wall connections

## Slide 21: Nuclear Facilities (ACC NF)
CCB Side View – East (towards WCS)
Area for Warm Piping Penetration – above 4.5 m access door. Specific location TBD
SCK CEN/81506386

## Slide 22: Nuclear Facilities (ACC NF)
AUB Side View – West (towards QRB)
Area for Warm Piping Penetration – above 4.5 m access door. Specific location TBD
SCK CEN/81505064

## Slide 23: Separate Cryogenic Compressor Building
Cold Box room in AUB
SCK CEN/81503739

## Slide 24: Separate Cryogenic Compressor Building
Cold Box room in AUB
SCK CEN/81503739
Space for Horisontal Coldbox
Need to avoid structural beams ~5 m apart
Possible routing of warm piping via roof
  Preferred horizontal penetration
Access Door to small (2.5 m) for QRB move-in
  Removal of single panel (~5m vertical considered)
  Preferred option is rooftop access

## Slide 25: Nuclear Facilities (ACC NF)
SCK CEN/81504370
AUB Cros-section
Note Sloping Roof
Structural Support Roof (~5m apart)
QRB place between to maximize height

## Slide 26: ColdBox Room
AUB Cros-Section
SCK CEN/81506075
Coldbox Room
Structural Support Roof (~5m apart)

## Slide 27: Separate Cryogenic Compressor Building
Cold Box room in AUB
SCK CEN/81504187
Ground Floor – Coldbox
Roof - Coldbox

## Slide 28: WARM PIPE ROUTING
Through AUB routing (2 wall penetrations)
Via Roof (vertical penetration)
– more bends, avoid ACC NF SSC
Cold Box room in AUB towards CCB

## Slide 29
Master Plan – MINERVA (buildings)
Equipment – Move from South Side
SCK CEN/81504188
North View
South View
Cold Box Room
From LTU via RF Gallery
Cold Box Room
SCK CEN/81506074

## Slide 30: Building Architecture Requirements
Fixed dimensions of CCB (WCS) and AUB (Coldbox Room)
Coldbox move-in via roof – BA coordination during installation
Routing of internal (scope of piping (AUB to CCB))
  Penetrations and ‘routing path’ for QPLANT Contractor
    Avoid ACC NF equipment and allow welding (15cm clearance for orbital welding)
Avoidance of oil spill and release to environment – CCB confinement
Additional noise mitigation – BA responsibility
Routing of QLR (from LTU to QRB)
Routing of additional warm piping
  Same as main cryogenic distribution (LTU to QRB)