## Slide 1: QSYS Buildings Overview (Masterplan Layout, Buildings, Rooms)
Daniel Berkowitz (MDB/ATS/ACR Unit)
Master Presentation

## Slide 2
SCK CEN Auxiliary Buildings
Document Reference and Navigation
Procurement drawings: SCK CEN/85102544
Similar to permit drawings, but more accurate
Used by the contractor to construct the building

## Slide 3
SCK CEN Auxiliary Buildings
Document Reference and Navigation
Doc no. | Document Name | Document Description | SCK CEN Reference
1 | QSYS Masterplan Layout & Buildings | Master Presentation | SCK CEN/46467661
2 | MINERVA_4NT_862356_000_00_TOTALDOC.pdf | Realistic Building Views | SCK CEN/83474410
3 | MINERVA_4NT_862354_000_00_TOTALDOC.pdf | Masterplan | SCK CEN/84582975
4 | BA_Dienstgebouw SCK CEN_TB_N_01_T2_versie20092023_.PDF.pdf | Project Zone | SCK CEN/81504499
5 | BA_SAB 1_P_N_00_Gelijkvloers.pdf | CCB + Outside Gas Storage | SCK CEN/81503739
6 | BA_SAB 1_P_N_02_Dakplan.pdf | CCB roof | SCK CEN/81505370
7 | BA_SAB 1_S_N_AA_Snede AA_.pdf | CCB section | SCK CEN/81505150
8 | BA_SAB 1_S_N_BB_Snede BB_.pdf | CCB section | SCK CEN/81506075
9 | BA_SAB 1_G_N_GO_Gevelzicht Oost.pdf | CCB side view | SCK CEN/81506386
10 | BA_SAB 2_G_N_GW_Gevelzicht West.pdf | AUB side view | SCK CEN/81505064
11 | BA_SAB 1_P_N_00_Gelijkvloers.pdf | AUB | SCK CEN/81503739
12 | BA_SAB 2_S_N_CC_Snede CC_.pdf | AUB section | SCK CEN/81504370
13 | BA_SAB 1_S_N_BB_Snede BB_.pdf | AUB section | SCK CEN/81506075
14 | BA_SAB 2_P_N_02_Dakplan.pdf | AUB roof | SCK CEN/81504187
15 | BA_SAB 2_G_N_GN_Gevelzicht Noord.pdf | AUB side view | SCK CEN/81504188
16 | BA_SAB 2_G_N_GZ_Gevelzicht Zuid.pdf | AUB side view | SCK CEN/81506074
Mostly used for QPLANT Tender

## Slide 4
QVB
QVB
QVE
QLM
QRB
WCS
WSH
WSH
WSH
QM
QM
QCELL
WPS
Cryoplant & Infrastructure
Cryo Backbone (QDB)
Cryomodules
CCB
AUB.xxx
LTU

## Slide 5: 1. Buildings Masterplan

## Slide 6
3D model
SC LINAC
Injector
RF Gallery
AUB Building
CCB Building

## Slide 7
Buildings Masterplan
=NA.BA_CDA514-Building layout NF ACC - Plan-level 0
LTU
RF Gallery
AUB Building
CCB Building

## Slide 8: QSYS Buildings

## Slide 9
SCK CEN/83474410
Buildings - Level 0
QSYS Buildings
MYRRHA
Reactor
Phase 1
Warm Compressor Station (WCS)
Warm Gas Storage (WSG)
Refrigerator Coldbox (QRB)
Main Cryolyne (QLM)
Cryocells (QCELL)
End Box (QVE)

## Slide 10
Buildings - Level 0
6
5
4
1
3
2
SCK CEN/83474410
QSYS Buildings (QB_x)
High Stakes:
Main Equipment installed on premise
Low Stakes:
Only peripherals or routing pipes
7
# | Building | QSYS top-level (*main) | QSYS Equipment
QB_1 | LTU/interior | QCELL* QDIST QINFRA | QM QVB QVE QLM WPS
QB_2 | LTU/Chicane | QDIST* QINFRA | QLM WPS
QB_3 | SAB2/RF-Gallery | QDIST* QINFRA | QLM WPS
QB_4 | SAB2/QRB Room | QPLANT QDIST QINFRA | QRB WPS QLM
QB_5 | SAB2/Other | QPLANT QINFRA? | WCS WPS?
QB_6 | SAB1/CCB | QPLANT QINFRA | WCS WSH
QB_7 | LTU/vents | QINFRA | WPS
QB_8 | SAB2/RF-Gallery | QCELL QDIST QINFRA | QC_int
QSYS is spread across SAB1, SAB2, and LTU
QSYS has high stakes when main equipment is installed, and low stakes when it is used for routing or peripherals
8

## Slide 11
QSYS Buildings
=NA.BA_CDA514-Building layout NF ACC - Plan-level 0
6
5
4
1
3
2
8
7

## Slide 12
2.3
QDB Segmentation
The QDB has 2 main segments (LTU and non-LTU), with 4 and 3 subsegments respectively.
The VLP-flow direction is the reference direction for all orientation and segmentation conventions.
When producing cross-sections or views, the observer is always “looking in the VLP-flow direction” (i.e., the VLP-flow goes into the screen).
Spools
Each spool is defined by two flanges: Flange A and Flange B
  Flange A is the upstream flange (i.e., first in the VLP-flow direction), and Flange B is downstream
  A QLM spool belongs to the section where its Flange A is located.
QDB Segmentation (colloquial term)
2.2
2.1
1.4
1.3
QDB Segment 1.2
1.1
Corresponds to location LB-S01 to S24
SB-LB01
LB-S25 to S30
TS-S01 to S03
Chicane Room
AUB Hallway
QRB Room
From ALX/46467661

## Slide 13: QDB Sectorization
Section 3
Section 4
Section 5
Section 6
Section 7
Section 2
Section 1
QDB Sectorization
Section names follow the convention: Section 1, Section 2, Section 3, etc.
The VLP-flow direction is the reference direction for all orientation and sectioning conventions.
When producing cross-sections or views, the observer is always “looking in the VLP-flow direction” (i.e., the VLP-flow goes into the screen).
Spools
Each spool is defined by two flanges: Flange A and Flange B
  Flange A is the upstream flange (i.e., first in the VLP-flow direction), and Flange B is downstream
  A QLM spool belongs to the section where its Flange A is located.

## Slide 14
Fixed Building dimensions!
WCS
QRB
WSH
QSYS Buildings
FYI,
=NA.BA_CDA514 – Building layout NF ACC - Plan - Level 0.pdf https://ecm.sckcen.be/OTCS/llisapi.dll/link/81841578

## Slide 15: WPS Lines (Warm Piping System)
S
LTU
RF Gallery
Chicane
Cold Box Room
QRB
QVE
QLM
From QCELL #1
W
On purpose, we do not show here the connections of the main He process to S or V
To HP of WCS inlet (+ reheater)
To HP of WCS inlet
VQCELL#24
VQCELLx
VQVE
QCELL # xx
QCELL # 24
From QLM INVAC x2
From QM INVAC
From QM INVAC
Or #12 ?
A
B
D
E
V
LTU Shielding

## Slide 16: QB_1 – LTU/interior
QB_1 Scope
QB_7 Scope
QB_2 Scope
QB_3 Scope
LTU interior
LTU roof
LTU chicane
SAB2/AUB
QCELL 30-25
QCELL 24 to 01
QVE
QLM
QLM
QVB24
QM24
QMj
QVBj
QM01
QVB01
QVE
W
S
U

## Slide 17: QB_2 – LTU/chicane
QB_1 Scope
QB_3 Scope
LTU interior
LTU chicane
SAB2/AUB
QLM
W
S
U
QB_2 Scope

## Slide 18
SCK CEN/81503739
Overview of QSYS Headers
LTU
S
Chicane
RF Gallery
QRB Room
31x lines (TBC)
W
U
A
B
D
E
QLM
Quantity TBC
V
V
V

## Slide 19
Fixed dimensions of CCB (WCS) and AUB (Coldbox Room)
Coldbox move-in via roof – BA coordination during installation
Routing of internal (scope of piping (AUB to CCB))
  Penetrations and ‘routing path’ for QPLANT Contractor
    Avoid ACC NF equipment and allow welding (15cm clearance for orbital welding)
Avoidance of oil spill and release to environment – CCB confinement
Additional noise mitigation – BA responsibility
Routing of QLR (from LTU to QRB)
Routing of additional warm piping
  Same as main cryogenic distribution (LTU to QRB)
Building Architecture Requirements

## Slide 20: 2b. Buildings for QDB

## Slide 21: 2c. LTU (QSYS specific)

## Slide 22: 3a. CCB Building (for WCS)

## Slide 23
Building design ready for start of detailed-design-for-procurement
SCK CEN/81503739
CCB - Dimensions
Room for WCS Components (scope QSYS/QPLANT)
Dedicated electrical equipment for WCS (scope NFS)
Space for WSH (scope QSYS/QINFRA)

## Slide 24
SCK CEN/81503739
CCB – Cross-sections
WCS
Dedicated Electrical Room for WCS
AA’
BB’

## Slide 25
Side View – East (towards WCS)
Area for Warm Piping Penetration – above 4.5 m access door. Specific location TBD
SCK CEN/81506386
CCB – Cross-sections

## Slide 26
Door Access for biggest equipment – HP compressor Skids
Noise Abatement (75 dB loudest equipment)
Design to prevent oil (oil lubricated compressors) contamination to outside
  Individual drip pans for HP and PVPS TBD
CCB – Room details
Room for WCS Components (scope QSYS/QPLANT)

## Slide 27
Space for 3x120 m³ Helium storage vessels (WGS)
Space for 1x30 ton Liquid Nitrogen and Evaporator (Not ACC NF scope
Access for truck inside and/or via wall connections
CCB – Exterior Details
Space for WSH (scope QSYS/QINFRA)

## Slide 28: 3b. AUB Rooms (for QRB)

## Slide 29
SCK CEN/81503739
AUB for QRB
Room for QRB Components (scope QSYS/QPLANT)

## Slide 30
SCK CEN/81503739
Space for Horisontal Coldbox
Need to avoid structural beams ~5 m apart
Possible routing of warm piping via roof
  Preferred horizontal penetration
Access Door to small (2.5 m) for QRB move-in
  Removal of single panel (~5m vertical considered)
  Preferred option is rooftop access
AUB for QRB - Room Dimensions
Room for QRB Components (scope QSYS/QPLANT)

## Slide 31
AUB Side View – West (towards QRB)
Area for Warm Piping Penetration – above 4.5 m access door. Specific location TBD
SCK CEN/81505064
AUB for QRB -

## Slide 32: Nuclear Facilities (ACC NF)
SCK CEN/81504370
AUB Cros-section
Note Sloping Roof
Structural Support Roof (~5m apart)
QRB place between to maximize height

## Slide 33: ColdBox Room
AUB Cros-Section
SCK CEN/81506075
Coldbox Room
Structural Support Roof (~5m apart)

## Slide 34: Separate Cryogenic Compressor Building
Cold Box room in AUB
SCK CEN/81504187
Ground Floor – Coldbox
Roof - Coldbox

## Slide 35: WARM PIPE ROUTING
Through AUB routing (2 wall penetrations)
Via Roof (vertical penetration)
– more bends, avoid ACC NF SSC
Cold Box room in AUB towards CCB

## Slide 36
Equipment – Move from South Side
SCK CEN/81504188
North View
South View
Cold Box Room
From LTU via RF Gallery
Cold Box Room
SCK CEN/81506074
AUB for QRB – side views

## Slide 37: 4a. QRB Move In

## Slide 38: Cold Box - Dimensions
D = 3.5-4m
L = 11m
SCK CEN/81790617
Cold Box is largest item of QRB

## Slide 39: Cold Box - Transporting
SCK CEN/81790617
12 m available
QRB Move-in
QRB
Transport Positioning
Flatbed + Crane
QRB
L = 11m
D=3.5-4m

## Slide 40
Equipment – Move from South Side
SCK CEN/81504499

## Slide 41: Cold Box – Move into Building
NEEDS CRANE
SCK CEN/81504499
1) Unload from flatbed
2) Rotate
3 option A) Move Sideways
3 option B) Move through roof
Two possible options: 3A or 3B
  Note that 3B needs a crane

## Slide 42
Space between SAB and MINERVA (south) perimeter fencing for unloading and move-in (QRB specific)
Access for/to crane for lifting of QRB
  Present preference via Roof Access
  Weight <= 100 ton (expected ~70 ton)
Access for/to crane for lifting of WGS
  3 x 120 m³ gas storage vessels
Handling of instantaneous load on ground (QRB specific) – Road/Flat surfaces
Masterplan Requirements (ACC NF)

## Slide 43: Masterplan - MINERVA
SCK CEN/84582975

## Slide 44
Copyright © SCK CEN - 2020
All property rights and copyright are reserved.
This presentation contains data, information and formats for dedicated use only and may not be communicated, copied, reproduced, distributed or cited without the explicit written permission of SCK CEN.
If this explicit written permission has been obtained, please reference the author, followed by ‘by courtesy of SCK CEN’.
Any infringement to this rule is illegal and entitles to claim damages from the infringer, without prejudice to any other right in case of granting a patent or registration in the field of intellectual property.
SCK CEN
Belgian Nuclear Research Centre
Studiecentrum voor Kernenergie
Centre d'Etude de l'Energie Nucléaire
Foundation of Public Utility
Stichting van Openbaar Nut
Fondation d'Utilité Publique
Registered Office:
Avenue Herrmann-Debrouxlaan 40 - 1160 BRUSSELS - Belgium
Research Centres:
Boeretang 200 - 2400 MOL - Belgium
Chemin du Cyclotron 6 - 1348 Ottignies-Louvain-la-Neuve - Belgium
44