## Slide 1: QSYS – Qualification and Commissioning Overview
Daniel Berkowitz (ATS/ACR)

## Slide 2
QSYS – System Breakdown
QVB
QVB
QVE
QLM
QRB
WCS
WSH
WSH
WSH
QM
QM
QCELL
WPS
Cryoplant & Infrastructure
Cryo Backbone
Cryomodules

## Slide 3: Definitions

## Slide 4
Q&C Campaign
Qualification (Validation of Equipment & Systems)
  Goal: Ensure the system meets predefined specifications.
  Notes: Can be done at any point.
  Aspects:
  Design Qualification (DQ) – Confirms the design meets the required standards.
  Installation Qualification (IQ) – Verifies proper installation (punching list)
    E.g. leak test, presence of all equipment
  Operational Qualification (OQ) – Ensures the system functions as intended.
  Performance Qualification (PQ) – Confirms consistent performance under real conditions.
Commissioning (Readiness for Operation)
  Goal: Systematic process of starting up and testing equipment and systems.
  Notes: The system has been installed on its final place and won’t be moved anymore
  Aspects:
  Commissioning Warm & w/o process fluid – Testing without process fluid (e.g., dry runs, control system validation), can be virtual or with true sensors
  Commissioning Warm & w/ process fluid – Testing with operational fluids.
  Commissioning Cold & w/ process fluid – Testing with operational fluids.
Q&C Campaign: Qualification and Commissioning
Q or C 1. 1.x = standalone w/o CIS
Q or C 1.2.x = standalone w/ CIS
Q or C 2.2.x = integrated with X
Q or C 3.2.x = integrated with X + Y
…
Highlighted differences VS qualification
Installation at final location (not planned to move it again)
Automated controls ready for startup  supply the users
The qualification is to check the specs against measurements
You can commission a system that does not meet the specs
Typical steps that can be performed in both qualification and commissioning
Purging and conditioning
Calibration and zero, on site ?

## Slide 5
FAT and SAT
FAT & SAT  These are contractual terms
SAT is only for the green and is contractual
FAT/SAT is accepting the activities
SAT is a subset of commissioning campaign
Q&C (Qualification and Commissioning)
This is the general term
Often confused with SAT, but it contains more than just acceptance testing

## Slide 6: REX from ESS

## Slide 7
  https://myrrha.atlassian.net/wiki/spaces/ACR/pages/1348960330/2025-03-27+ESS+REX+from+Philipp
2025-03-27 Discussion with Philipp
To read absolutely

## Slide 8
2023-12-50 - Strategy and installation experience for ESS SRF linac.pptx
To read absolutely

## Slide 9
ESS book
ESS Book - Chapter 3 Final.pdf https://ecm.sckcen.be/OTCS/llisapi.dll/link/91586851
To read absolutely

## Slide 10: Other papers from ESS (Philipp)
Overall Cryo process design:
ESS Cryogenic System Process Design - IOPscience
Recovery, purification: https://iopscience.iop.org/article/10.1088/1757-899X/755/1/012095
Cryoplant controls: ESS Cryogenic Controls Design - EPJ Techniques and Instrumentation
Cryoplant specification: https://www.sciencedirect.com/science/article/pii/S1875389215003971
Safety helium collector for burst disks: https://iopscience.iop.org/article/10.1088/1757-899X/502/1/012132
Safety relief line, helium guard, recovery:
Helium Management of ESS Cryoplants with Common Safety Relief Header and Recovery System - IOPscience
Cryoplant commissioning:
Commissioning of the Large-Scale 2 K Helium Refrigeration System
Also, there are more recent, accepted but not yet published papers on cryo controls for CMs/CDS, commissioning experience with CDS and a whole book on ESS cryogenics edited by John Weisend.

## Slide 11: Paper 1
This paper describes two different series of test cases developed for the ACCP-CDS assembly, one to be conducted at 8K feed temperature and over-atmospheric pressure to determine the CDS heat load and the other at 2 K equivalent sub-atmospheric conditions with the cold compressors (CCs) in operation to check their performance with the CDS attached.
The new developed control logic, limitations and the interface parameters will be discussed.
2022 - Zhang - Test preparation of ESS cryoplant and distribution.pdf
they did a cold pre-qualification of their QDB. i mean, cold test before installation

## Slide 12
2. Commissioning preparation
It is by far easier to conduct most tests and qualify the CDS before the cryomodules (CMs) were, connected. Instead of CMs there were endcaps connected at the valvebox
One type of these tests were measurements of the control valves seat leaks which are quicker and easier if done with a small test volume of the U-tubes instead of a full cryomodule attached. Many leaks were detected predominantly in the elliptical part of the CDS which still need to be completely understood and rectified.
Before that, the pressure transmitters had to be calibrated by first pumping the system down for adjusting the zero and then pressurising for the full operation span
Both, lowest pressure at pumpdown and stability of the high pressure, can be used to get an idea of the overall system leak tightness to air or to the helium recovery system
Verifying the individual curve and wire connection for each of the CERNOX sensors in the CDS. A number of issues were detected as uploading the wrong calibration curve or mixing up, wrongly connected wires or short circuits
Summary (at warm)
Valve leak test (easier with small volumes)
  By temperature or pressure ?
Calibration of pressure transmitters
Overall system leak tightness w/o CM
CERNOX calibration curve and cabling check
2024 - Commissioning of the cryogenic distribution of the ESS Linac.pdf

## Slide 13
The feed at 8K without LHe Dewar and phase separator sub-cooler is a special operations mode that had been developed with the cryoplant supplier Linde Kryotechnik before the testing started so this special mode was needed, why ?
A first inspection after temperature stabilization but before cooldown completion did not reveal severe cold spots or moisture formation on the long cryoline, however some cold spots on valveboxes due to heat conduction.
Even though the detected issues, particularly the valve TAO, were substantial, we proceeded with heat load determination to find out more about the system, it’s capabilities and limitations.
To determine the overall heat load of the CDS without CMs and its liquid helium vessels, we operated the system at 8K, making sure to have one phase and sensible heat to deal with only. Okay, but in normal operation, this is also what we get ..
Also, we wanted to test in a temperature range yielding moderate specific heat capacity gradients and consequently better resolution of the temperature measurements ok so this mode is mainly for better resolution, not because there is no other way since no phase separator ,
Summary (at cold)
Cold spots
TAOs in the Ell VBX
Static heat loads at 8 K
2024 - Commissioning of the cryogenic distribution of the ESS Linac.pdf

## Slide 14: QSYS Q&C Campaigns

## Slide 15
QSYS – Q&C, the “reference cold process campaigns”
WHS
QCELL # xx
QLM
QVE
QRB
WCS
WPS
WHS
QCELL # xx
QLM
QVE
QRB
WCS
WPS
WHS
QCELL # xx
QLM
QVE
QRB
WCS
WPS
1. QPLANT alone
2. QPLANT + WPS + headers
3. QPLANT + WPS + header + branches
We plan for the 24x QCELLs for now
Possible to test up to the flow of 30x QCELLs
Here the QPLANT has already history, so we don’t start from scratch
Performance was tested, we now have more noise because of the volumes downstream
The QPLANT learns to cope with a user, maybe tweak the gains
Cooling power
Cold compressor flow
QM not installed yet
QM not installed yet
Test Cap
Test Cap

## Slide 16
QSYS – Q&C, the “reference process campaigns”
4. QSYS (QPLANT + QDB + QMs + WPS)
xxx
WHS
QCELL # xx
QLM
QVE
QRB
WCS
WPS

## Slide 17: Test list documentation
Those lists shall indicate
  What we want to test
  When we want (need) to have the test
QM Q test list (ALX 84658439)
  Content
    The proposed FAT by RI
    The list of tests for FREIA
      Goal 1: SAT (contract)
      Goal 2: feedback for SCK CEN +
QDB and QPLANT Q&C test list (ALX 91139410)
  QPLANT Q&C (light summary, just for perspective)
  QPLANT Q&C
    FAT at vendor premise, SAT

## Slide 18: QPLANT + QDB SAT overview
QPLANT commissioning phases
  QPLANT Q&C 1.1 = decided for sure
    Tests: cooling power, not the efficiency
      Threshold on the Cooling power
      We make sure the COP is > xxx (rough, don’t pinpoint)
    Simulate main: flow 45 g/s on A-B circuits (heater)
    TS and coupler loops? Probably not the flow  qualitatively, not quantitative
    QRB has dummy cap + heat loads
    QRB has all instrumentation needed
  What about CIS of the QPLANT ? 1.2 or 2.2 ?
QPLANT C 2.2 (in // to QDB SAT 2.1 ?)
    Main loop (A-B): all on QVE  to compare to Q&C 1.1
      Need for a 900 W heater set, split in 6x (ACS solution)
      Need for 2x valves inlet, 2x valve outlet (ACS solution)
    TS loop (D-E): not possible to have 8500 W on QVE only  “dilute” on QVBs
      Already 5100 W: 4800 W on QVB passthroughs + 300 W on QVE (passthrough + main TS)
      60% for free  enough ?
    Coupler loop: not planned
QPLANT C 3.2 (in // to QDB SAT 1.2)
    Main loop: same as QPLANT SAT 1.2  all through QVE
    TS loop: additional 4800 W on QVB TS (200 W per TS)  10100 W in total on TS
    Coupler loop: need test cap 2b or +
Emulating A-B is fine
Not D-E
Liquefaction load as well (W) TBC
Emulating D-E and W ?
SAT (QPLANT) all in one contractually
SAT (QDB) = installation and design qualification but not operation (the contractor don’t take the responsibility to operatre
17 % capacity of QPLANT is from the QDB
“odd conditions” for QDB testing
A: 3 bar 7 K  OK
B: 1 bar 9 K  OK, not engage the cold CMPs
Emulating A-B: is it needed for QPLANT Q&C ? Not sure
So, what is needed for QDB Q&C ?

## Slide 19
CIS
QPLANT – Q&C
WHS
QCELL # xx
QLM
QVE
QRB
WCS
WPS
QDB/QM is out of scope (may not even be there yet)
Q&C 1.1
Stand-alone
WHS
QCELL # xx
QLM
QVE
QRB
WCS
WPS
QDB/QM is out of scope (may not even be there yet)
Q&C 1.2
Stand-alone
QPLANT SAT
Contractor internal business
For CIS
Only a communication test (query/reply)
  I/O
  Commands
  Data (status, interlocks, …)
Out of scope is debugging of CIS
Contractually, SAT program is done in one big Campaign
Contractor shall prove full Q&C (= Q&C 1.1)
Up to Contractor if they want to run this phase in stand-alone
Q&C 1.3
Stand-alone
WHS
QCELL # xx
QLM
QVE
QRB
WCS
WPS
QDB/QM is out of scope (may not even be there yet)
CIS
CIS
For CIS
Finalize Q&C on its own system.
For QPLANT Contractor
Assist as part of SLA and SPC (Support Contract, hourly rate)
19-03-2025: discussed by DBE & UDO
QPLANT:CS
QPLANT:CS
QPLANT:CS
Part of SLA and SPC
SLA = Service Level Agreement
Contractor ensures system works
Metric is the “uptime” of the system
Flat-rate cost
They solve the issues as needed
QPLANT Tender
It is a Contingent Part (we may or may-not buy it)
SPC = Support Contract
Contractor is available on request
Metric is ad-hoc by SCK
Cost is based on effort (i.e. hourly rate)
They solve the issues when requested
QPLANT Tender
In the offer, the Applicant shall provide details -> fixed part
Test Cap
Test Cap
Test Cap

## Slide 20
QDB – Q&C
WHS
QCELL # xx
QLM
QVE
QRB
WCS
WPS
3.2 QPLANT + WPS + header + branches
QM not installed yet
WHS
QCELL # xx
QLM
QVE
QRB
WCS
WPS
2.1 QDB only
Needed: QDB only, at warm & w/o process fluids
Part of the QDB Operation Qualification: Valves, Instrumentation, Leaks (INVAC-Air, INVAC-He, He-He)
Not needed yet: QPLANT, QDB:CS, WPS, QMs
Contractor leads and SCK CEN witnesses
QM not installed yet
QPLANT is out of scope (may not even be there yet)
QDB
SAT1
Test Ca Lvl2p
QDB
Cold test
At cold & with process fluids
Needed: QPLANT, QDB:CS, WPS
Helps early identification of “cold issues”, both for all SAT1-components and some of the SAT2-components
SCK CEN runs: SCK CEN experts + operators will actuate the process
Test plan is on SCK CEN responsibility with inputs (limitations) from Contractor.
Contractor: they have to give us the “manual”  the “as-built” specification (so we don’t break the equipment)
Contractor witnesses the commissioning and trains SCK CEN personnel on “firsts”. Need an expert to be present during cold tests and have technicians that can come within a day
Test Cap Lvl1
WHS
QCELL # xx
QLM
QVE
QRB
WCS
WPS
4.1. QPLANT + WPS + header + branches
QDB
SAT2
Here QSYS is fully there
We SAT: QRB & QM welds, PeMos, cold issues of SAT2-componets
Cold issues of “SAT1-components” are scope of warranty
Commissioning
Leader: Contractor
Witness: SCK CEN
Operator: Contractor
Leader: Contractor
Witness: SCK CEN
Operator: SCK CEN
Leader: SCK CEN Witness: Contractor
Operator: SCK CEN
/!\ Warranty of SAT1

## Slide 21
QDB – Q&C Gantt Chart
Installation
Phases A-B-C
Commissioning
SAT2
Installation Phase A (pre-SAT1)
Only Backbone Elements
Only elements that are scope of QDB Tender.
  QLM spools
  All QVBs
  Test caps (!)
  QVE
  PeMo whenever applicable
No external interfaces. Thus, independent from other QSYS equipment.
Excludes: Chimmney welds, QRB welds
QDB Cold Testing
Operated by SCK
Contractor withnesses
Cold-issues:
  If on SAT1-component: Contractor fixes as part of warranty
  If on SAT2-component: Contractor fixes as preparation towards SAT2
Installation Phase C
24x QM-Chimey welds
Remaining PeMos
QDB Cold Testing Scenario A
QDB Cold Testing Scenario B
Installation Phase B
QRB-welds
Interfaces to site infrastructure
Plugging cables to patchbox
.....
SAT1

## Slide 22
At cold & with process fluids
Needed: QPLANT, QDB:CS, WPS
Goal
  Helps early identification of “cold issues”, both for all SAT1-components and some of the SAT2-components
  Qualification: component performance at cold + controls
Major steps
  Step 1: headers only
  Ste
SCK CEN runs: SCK CEN experts + operators will actuate the process
Test plan is on SCK CEN responsibility with inputs (limitations) from Contractor.
Contractor: they have to give us the “manual”  the “as-built” specification (so we don’t break the equipment)
Contractor witnesses the commissioning and trains SCK CEN personnel on “firsts”. Need an expert to be present during cold tests and have technicians that can come within a day
QDB Cold test – details
WHS
QCELL # xx
QLM
QVE
QRB
WCS
WPS
QM not installed yet
Test Ca Lvl2p

## Slide 23
Get the full REX from ESS  Philipp
Finish the test list on both QPLANT and QDB/QM sides
  Try to identify what is needed and when
Approach for the test caps and QVE instrumentation
  Can be simple, if we don’t manage to define them fully
    Max instrumentation
    Can be added later
  Same for QVE
2025-03-26 Next move

## Slide 25: Test system vs simulator
First estimate of possible test - ACR to define more
Type of test. Test System, System Under Test - Output to provide expected representative value
Confluence Minutes 2024-11-27

## Slide 26: Test system vs simulator
A System (i.e. QCELL)
.HW
  .MH
  .PH
.CS
.IS
.SW
.ELEC
.CIRc

## Slide 27
Copyright © SCK CEN
All property rights and copyright are reserved.
This presentation contains data, information and formats for dedicated use only and may not be communicated, copied, reproduced, distributed or cited without the explicit written permission of SCK CEN.
If this explicit written permission has been obtained, please reference the author, followed by ‘by courtesy of SCK CEN’.
Any infringement to this rule is illegal and entitles to claim damages from the infringer, without prejudice to any other right in case of granting a patent or registration in the field of intellectual property.
SCK CEN
Belgian Nuclear Research Centre
Studiecentrum voor Kernenergie
Centre d'Etude de l'Energie Nucléaire
Foundation of Public Utility
Stichting van Openbaar Nut
Fondation d'Utilité Publique
Registered Office:
Avenue Herrmann-Debrouxlaan 40 - 1160 BRUSSELS - Belgium
Research Centres:
Boeretang 200 - 2400 MOL - Belgium
Chemin du Cyclotron 6 - 1348 Ottignies-Louvain-la-Neuve - Belgium

## Slide 28
QSYS – x
QCELL # xx
QLM
QVE
QRB
A
B
D
E
WCS
A-B
D-E
W
QLM
QCELL
QVE
WCS
S
W
WHS
WPS